## Sheet1
EQUIPMENT ITEM | ECONOMIC LIFE (YEARS)
ABSORPTION LIQUID CHILLING SYSTEM | 20
AIR COMPRESSORS | 20
AIR CONDITIONER SINGLE PACKAGE, AIR–COOLED, HERMETIC | 10
AIR CONDITIONER WITH REMOTE AIR–COOLED CONDENSER | 10
AIR–COOLED SPLIT SYSTEM AIR CONDITIONERS | 10
AIR HANDLING UNITS HORIZONTAL AND VERTICAL | 20–25
BOILERS | 20–25
BURNERS | 10
CENTRAL STATION UNITS | 20
CENTRIFUGAL CHILLERS | 20–30
CENTRIFUGAL COMPRESSORS, MULTISTAGE | 15–20
CENTRIFUGAL COMPRESSORS, SINGLE STAGE | 20
CENTRIFUGAL LIQUID CHILLING SYSTEMS | 20–30
CHILLERS, ABSORPTION | 20
CHILLERS, RECIPROCATING, UP TO 150 TR | 15–20
CHILLERS, RECIPROCATING, 150 TR AND UP | 15–20
COILS, HEATING AND COOLING | 30
COMM. AIR CONDITIONERS, REMOTE A.C. CONDENSER | 10
COMM. WATER–COOLED CONDITIONERS, SINGLE PACKAGE | 10
COMPRESSORS, RECIPROCATING V/W, HERMETIC | 12
COMPRESSORS, RECIPROCATING V/W, OPEN | 14
COMPRESSOR UNITS, VERTICAL SINGLE–ACTING | 30
CONDENSERS, EVAPORATIVE | 20
CONDENSERS, HORIZONTAL SHELL AND TUBE | 20
CONDENSERS, REMOTE AIR–COOLED | 12
CONDENSING UNITS, RECIPROCATING V/W, HERMETIC | 12
CONDENSING UNITS, RECIPROCATING V/W, OPEN | 14
CONDENSING UNITS, VERTICAL SINGLE–ACTING | 30
CONTROLS, ELECTRIC AND PNEUMATIC | 20
COOLING COILS | 30
COOLING TOWERS, MASONRY FILL | 45
COOLING TOWERS, METAL FILL | 15–20
COOLING TOWERS, WOOD FILL | 15–20
DIESEL ENGINES | 10–12
ELECTRIC FURNACES | 10
ELECTRIC HEATING, ADD ON | 10
ELECTRIC MOTORS | 20–25
FANS, BACKWARD CURVED (AIRFOIL) | 20
FANS, COIL MULTIPLE SPACE CONDITIONS | 20
FANS, COIL MULTIPLE SPACE CONDITIONS | 20
FAN COIL ROOM CONDITIONS | 20
FANS, FORWARD CURVED | 20
FANS, UTILITY SETS | 20
FURNACES, GAS FIRED | 10–15
FURNACES, OIL FIRED | 10–15
GASOLINE ENGINES | 10
HEAT PUMPS, SINGLE PACKAGE, AIR–TO–AIR | 20
HEAT PUMPS, SINGLE PACKAGE, WATER–TO–AIR | 20
HEAT PUMPS, SPLIT SYSTEM, AIR–TO–AIR | 20
HIGH PRESSURE RECEIVERS | 30
HORIZONTAL SHELL AND TUBE CONDENSERS | 30
INDUCTION ROOM AIR UNITS | 30
LIQUID CHILLING SYSTEMS, CENTRIFUGAL | 20
LIQUID COOLERS, HORIZONTAL SHELL AND TUBE | 30
LOW TEMPERATURE COMPRESSOR UNITS, RECIP. V/W, HERMETIC | 12
LOW TEMPERATURE COMPRESSOR UNITS, RECIP, V/W, OPEN 14 | 14
MULTISTAGE TURBO COMPRESSORS 20 | 20
MULTIZONE CENTRAL STATION UNITS 20 | 20
MULTIZONE ROOFTOP UNITS 10 | 10
MULTIPLE SPACE FAN COIL UNITS 20 | 20
OIL FIRED FURNACES 10 | 10
OIL RECEIVERS | 5–10
PACKAGED REFRIGERATION UNITS 12 | 12
PACKAGED TERMINAL UNITS 10 | 10
PLUG TYPE, REFRIGERATION UNITS 12 | 12
PRODUCE STORAGE UNITS 12 | 12
PRODUCT COOLERS 20 | 20
PRODUCT COOLERS, AMMONIA 20 | 20
PUMPS, CENTRIFUGAL | 20–25
RESIDENTIAL WATER–COOLED CONDITIONERS, SINGLE PACKAGE 10 | 10
REMOTE AIR–COOLED CONDENSER 12 | 12
ROOM AIR CONDITIONERS 8 | 8
ROOM UNITS 8 | 8
TURBINES (STEAM) | 10–30